## Form
|  | Blue Solar charge controller MPPT |  |  |  |  | Fourchette de tension |  | Fourchette de courant
1
| Panneau: | 24
| En serie: | 3 |  | Parallèle: | 4
| Puissance PV totale @STC: | 3120 | Wc
| Température Paneau: | Min. | 0 | Max. | 70 |  |  | 2.5
|  |  | 25 |  |  |  | 12 | 4
| Régulateur: | 10 |  |  |  |  | 24 | 6
[7 empty] | 36 | 10
| Tension du système: |  | 4 | Volt |  |  | 48 | 16
25
| Longueur cable, Paneaux à MPPT * |  | 10 | Section: | 6 | 3 |  | 35
* La distance simple
| Tension d'entrée max.: |  |  | 150
| PV tension max. @ temp. min. |  |  | 122.7555
| Tension d'entrée min. @ MPP |  |  | 49
| PV tension min. @ temp. max. |  |  | 72.7376
| Courant de sortie max. |  |  | 70
| Courant max. @ MPP temp. min. |  |  | 69.4352
| Courant max. @ MPP temp. max. |  |  | 53.3498
| Configuration du panneau |  |  | Accepté | Accepté | PAS accepté
BHO 11-2017 2.7
Les panneaux PV sont-ils souvent couverts de neige ? | [5 empty] | Non | FALSE
Exemple de localisation de site avec la température attendue: |  |  |  |  | Min. | Max.
À plat sur toit de camping-car toute l'année (mauvaise ventilation) |  |  |  |  | 0 | 70
À plat sur camping-car , seulement l'été (mauvaise ventilation) |  |  |  |  | 15 | 70
À plat sur ​​le bateau (mauvaise ventilation) |  |  |  |  | 10 | 65
Inclinée sur bateau (bonne ventilation) |  |  |  |  | 5 | 60
Toit en pente, en région chaude (bonne ventilation) |  |  |  |  | 5 | 70
Toit en pente, région tempérée (bonne ventilation) |  |  |  |  | 0 | 65
Toit en pente, en montagne (bonne ventilation) |  |  |  |  | -5 | 60

## Modules
| Manufacturer | Type | Power | Vmpp | Impp | Voc | Isc | V temp coeff | I temp coeff | Art.Nr.
| [name] | [name] | [W] | [V] | [A] | [V] | [A] | [%/°C] | [%/°C]
Victron Energy SPM30-12 (SPM030301200) | Victron Energy | SPM30-12 | 30 | 18 | 1.67 | 22.5 | 2 | -0.34 | 0.037 | SPM030301200
Victron Energy SPM50-12 (SPM030501200) | Victron Energy | SPM50-12 | 50 | 18 | 2.78 | 22.2 | 3.16 | -0.34 | 0.037 | SPM030501200
Victron Energy SPM80-12 (SPM030801200) | Victron Energy | SPM80-12 | 80 | 18 | 4.45 | 22.3 | 4.96 | -0.34 | 0.037 | SPM030801200
Victron Energy SPM100-12 (SPM031001200) | Victron Energy | SPM100-12 | 100 | 18 | 5.56 | 22.4 | 6.53 | -0.34 | 0.037 | SPM031001200
Victron Energy SPM150-12 (SPM031501200) | Victron Energy | SPM150-12 | 150 | 18 | 8.33 | 22.4 | 9.8 | -0.34 | 0.05 | SPM031501200
Victron Energy SPM190-24 (SPM031902400) | Victron Energy | SPM190-24 | 190 | 36 | 5.44 | 43.2 | 5.98 | -0.34 | 0.037 | SPM031902400
Victron Energy SPM300-24 (SPM033002400 ) | Victron Energy | SPM300-24 | 300 | 36 | 8.06 | 45.5 | 8.56 | -0.34 | 0.037 | SPM033002400
Victron Energy SPP20-12 (SPP030201200) | Victron Energy | SPP20-12 | 20 | 18 | 1.11 | 22.5 | 1.23 | -0.34 | 0.045 | SPP030201200
Victron Energy SPP30-12 (SPP030301200) | Victron Energy | SPP30-12 | 30 | 18 | 1.67 | 22.5 | 1.85 | -0.34 | 0.037 | SPP030301200
Victron Energy SPP40-12 (SPP020401200) | Victron Energy | SPP40-12 | 40 | 18 | 2.22 | 22.5 | 2.45 | -0.34 | 0.037 | SPP020401200
Victron Energy SPP50-12 (SPP030501200) | Victron Energy | SPP50-12 | 50 | 18 | 2.78 | 22.2 | 3.09 | -0.34 | 0.037 | SPP030501200
Victron Energy SPP80-12 (SPP030801200) | Victron Energy | SPP80-12 | 80 | 18 | 4.44 | 21.6 | 5.06 | -0.34 | 0.037 | SPP030801200
Victron Energy SPP100-12 (SPP031001200) | Victron Energy | SPP100-12 | 100 | 18 | 5.56 | 21.6 | 6.32 | -0.35 | 0.037 | SPP031001200
Victron Energy SPP140-12 (SPP031401200) | Victron Energy | SPP140-12 | 140 | 20 | 7.78 | 21.6 | 8.85 | -0.35 | 0.037 | SPP031401200
Victron Energy SPP250-20 (SPP032502001) | Victron Energy | SPP250-20 | 250 | 30 | 8.33 | 36.01 | 9.4 | -0.34 | 0.045 | SPP032502001
Victron Energy SPP290-24 (SPP032902400) | Victron Energy | SPP290-24 | 290 | 36 | 8.06 | 44.1 | 8.56 | -0.34 | 0.045 | SPP032902400
SolarWorld 300W Mono () | SolarWorld | 300W Mono | 300 | 32.6 | 9.31 | 40 | 9.83 | -0.29 | 0.07
SolarWorld 280W Protect | SolarWorld | 280W Protect | 280 | 32.3 | 9.12 | 39.8 | 9.65 | -0.29 | 0.06
JA SOLAR 350W JAM6(K) 72-350/PR | JA SOLAR | 350W JAM6(K) 72-350/PR | 350 | 38.58 | 9.07 | 47.24 | 9.61 | -0.3 | 0.06
SUNPOWER 150W flexible | SUNPOWER | 150W flexible | 150 | 25.2 | 5.97 | 30.11 | 6.32 | -0.33 | 0.05
SUNPOWER 150W flexible ETFE | SUNPOWER | 150W flexible ETFE | 150 | 25.52 | 5.97 | 30.11 | 6.32 | -0.33 | 0.05
SUNPOWER 110W flexible ETFE | SUNPOWER | 110W flexible ETFE | 110 | 18.56 | 5.97 | 21.9 | 6.34 | -0.33 | 0.05
BENQ 333W | BENQ | 333W | 225 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
SOLARNOVA 260W | SOLARNOVA | 260W | 260 | 30.55 | 8.53 | 37.8 | 8.99 | -0.33 | 0.05
Custom: 9XYZ 9ABC | Custom: 9XYZ | 9ABC | 275 | 44.3 | 5.54 | 53 | 5.86 | -0.25 | 0.03
Custom: 10XYZ 10ABC | Custom: 10XYZ | 10ABC | 275 | 44.3 | 5.54 | 53 | 5.86 | -0.25 | 0.03
Custom: 11XYZ 11ABC | Custom: 11XYZ | 11ABC | 275 | 44.3 | 5.54 | 53 | 5.86 | -0.25 | 0.03
Coefficients de température:
Si vous avez le Coefficient de température à tension de circuit ouvert en mV/°C , voici comment changer ce coefficient en %/°C
Ecrire la valeur de la VOC en Volt: |  | 24.1 | V
Ecrire la valeur du coefficient en mV/°C: |  | -77 | mV/°C
La valeur du coefficient en %/°C est de: |  | -0.3195 | %/°C
Si vous avez le Coefficient de température à Courant de Court-Cicuit en mA/°C, voici comment changer ce coefficient en %/°C
Ecrire la valeur de Isc en Ampère: |  | 8.72 | A
Ecrire la valeur du coefficient en mA/°C: |  | 4.7 | mA/°C
La valeur du coefficient en %/°C est de : |  | 0.053899 | %/°C

## Regulator
| Manufacturer | Type | Power @ 12V | Power @ 24V | Power @ 36V | Power @ 48V | Voc max | Voc min | Vmpp min | System Voltage |  |  |  | IPV max | Ibat max | Efficiency@12 | Efficiency@24 | Efficiency@36 | Efficiency@48
Victron Energy Blue-/ SmartSolar MPPT 75/10 | Victron Energy | Blue-/ SmartSolar MPPT 75/10 | 135 | 270 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 13 | 10 | 0.98 | 0.98 | 0 | 0
Victron Energy Blue-/ SmartSolar MPPT 75/15 | Victron Energy | Blue-/ SmartSolar MPPT 75/15 | 200 | 400 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 15 | 0.98 | 0.98 | 0 | 0
Victron Energy Blue-/ SmartSolar MPPT 100/15 | Victron Energy | Blue-/ SmartSolar MPPT 100/15 | 200 | 400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 15 | 0.98 | 0.98 | 0 | 0
Victron Energy Smart Solar MPPT 100/20 | Victron Energy | Smart Solar MPPT 100/20 | 290 | 580 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 20 | 20 | 0.98 | 0.98 | 0 | 0
Victron Energy Blue-/ SmartSolar MPPT 100/30 | Victron Energy | Blue-/ SmartSolar MPPT 100/30 | 440 | 880 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 30 | 30 | 0.98 | 0.98 | 0 | 0
Victron Energy Blue-/ SmartSolar MPPT 100/50 | Victron Energy | Blue-/ SmartSolar MPPT 100/50 | 700 | 1400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 50 | 50 | 0.98 | 0.98 | 0 | 0
Victron Energy Blue-/ SmartSolar MPPT 150/35 | Victron Energy | Blue-/ SmartSolar MPPT 150/35 | 500 | 1000 | 1500 | 2000 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 40 | 35 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy BlueSolar MPPT 150/45 Tr/MC4 | Victron Energy | BlueSolar MPPT 150/45 Tr/MC4 | 650 | 1300 |  | 2600 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 50 | 45 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy BlueSolar MPPT 150/60 Tr/MC4 | Victron Energy | BlueSolar MPPT 150/60 Tr/MC4 | 860 | 1720 |  | 3440 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 50 | 60 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy BlueSolar MPPT 150/70 Tr/MC4 | Victron Energy | BlueSolar MPPT 150/70 Tr/MC4 | 1000 | 2000 |  | 4000 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 50 | 70 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy SmartSolar MPPT 150/85 Tr/MC4 | Victron Energy | SmartSolar MPPT 150/85 Tr/MC4 | 1200 | 2400 |  | 4900 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 85 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy SmartSolar MPPT 150/100 Tr/MC4 | Victron Energy | SmartSolar MPPT 150/100 Tr/MC4 | 1450 | 2900 |  | 5800 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 100 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy SmartSolar MPPT 250/60 Tr/MC4 | Victron Energy | SmartSolar MPPT 250/60 Tr/MC4 | 860 | 1720 |  | 3440 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 35 | 60 | 0.99 | 0.99 | 0.99 | 0.99
Victron Energy SmartSolar MPPT 250/70 Tr/MC4 | Victron Energy | SmartSolar MPPT 250/70 Tr/MC4 | 1000 | 2000 |  | 4000 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 35 | 70 | 0.99 | 0.99 | 0.99 | 0.99
Victron Energy SmartSolar MPPT 250/85 Tr/MC4 | Victron Energy | SmartSolar MPPT 250/85 Tr/MC4 | 1200 | 2400 |  | 4900 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 85 | 0.99 | 0.99 | 0.99 | 0.99
Victron Energy SmartSolar MPPT 250/100 Tr/MC4 | Victron Energy | SmartSolar MPPT 250/100 Tr/MC4 | 1450 | 2900 |  | 5800 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 100 | 0.99 | 0.99 | 0.99 | 0.99
Victron Energy BlueSolar MPPT 150/70 VE.Can | Victron Energy | BlueSolar MPPT 150/70 VE.Can | 1000 | 2000 | 3000 | 4000 | 150 | 7 | 2 | 12 | 24 | 36 | 48 | 50 | 70 | 0.95 | 0.965 | 0.97 | 0.975
Victron Energy BlueSolar MPPT 150/85 VE.Can | Victron Energy | BlueSolar MPPT 150/85 VE.Can | 1200 | 2400 | 3600 | 4850 | 150 | 7 | 2 | 12 | 24 | 36 | 48 | 70 | 85 | 0.95 | 0.965 | 0.97 | 0.975

## Calculation table
DATA:
Location: | 0 | min
| 70 | max
Module info: | 113.4 | Voc @25°C
| 91.65 | Vmpp @25°C
| 35.96 | Isc PV@25°C
| 34.12 | Impp PV @25°C
| 65.1479 | Impp output @25°C
| -0.33 | Temp. Coeff. Voc
| -0.37422 | Temp. Coeff. Voc absolute
| 0.05 | Temp. Coeff. Isc
| 0.01798 | Temp. Coeff. Isc absolute
| 3120 | Choosen PV power
Regulator info: | 150 | Voc max | 70 | Ibat max
| 53 | Voc min | 50 | IPV max
| 49 | Vmpp min | 48 | System voltage | 19
| 4000 | Possible charge power (from datasheet) without limiting PV power | 0.98 | Max. Efficiency
Voltage drop: | 0.0178 | Cupper resistance
| 0.059333 | Factor
RESULTS:
Temperature | Voc max. | Voc START min. | Vmpp RUN min. | String Voc max. | String Vmpp max. | String Vmpp corr.max. | String Voc min. | String Vmpp min. | String Vmpp corr. min.
0 | 150 | 53 | 49 | 122.7555 | 101.0055 | 99.0077
5 | 150 | 53 | 49 | 120.8844 | 99.1344 | 97.1313
10 | 150 | 53 | 49 | 119.0133 | 97.2633 | 95.2548
15 | 150 | 53 | 49 | 117.1422 | 95.3922 | 93.3784
55 | 150 | 53 | 49 |  |  |  | 102.1734 | 80.4234 | 78.3669
60 | 150 | 53 | 49 |  |  |  | 100.3023 | 78.5523 | 76.4905
65 | 150 | 53 | 49 |  |  |  | 98.4312 | 76.6812 | 74.6141
70 | 150 | 53 | 49 |  |  |  | 96.5601 | 74.8101 | 72.7376
Temperature | Ibat max. | Impp PV max. | System Voltage | Ibat max. @ Impp | Ibat min. @ Impp
0 | 70 | 33.6705 | 48 | 69.4352
5 | 70 | 33.7604 | 48 | 68.3308
10 | 70 | 33.8503 | 48 | 67.2197
15 | 70 | 33.9402 | 48 | 66.1016
55 | 70 | 34.6594 | 48 |  | 56.91
60 | 70 | 34.7493 | 48 |  | 55.7301
65 | 70 | 34.8392 | 48 |  | 54.5434
70 | 70 | 34.9291 | 48 |  | 53.3498
PV Power ratio | 0.78 | If more than 1.3 the user becomes an alert that he/ she is oversizing the PV generator with more than 30%
Maximum power point PV current is higher than maximum regulator input current |  |  | FALSE

## Version
History
2.7 | - Added 150Wp mono module, SmartSolar 250/60 & 70 and maximum input current
2.6 | - Added Smart Regulators and SmartSolar 100/20
2.5 | - Added translations for 'coefficient support' in the modules TAB
2.4 | - Bug fixed for max. charge current calculations
2.3 | - Replaced solar modules according newest list. Added 2 SmartSolar MPPT's 250/85 & 250/100 & a remark when the PV generator is oversized.
2.2 | - Added the MPPT 150/85 Tr/MC4 and 150/100 Tr/MC4 & added two cable sizes 16mm² & 35mm²
2.1 | - Added the Poly module with 190Wp & added the new VE.Direct MPPT's 150/45, 150/60 & 150/70, small correction in cable loss voltage
2.0 | - Added the MPPT 75/10 and took out the discontinued 75/50
1.9 | - Added new solar modules, and now 10 additional modules can be added instead of 3.
1.8 | - Added a small calculation on the 'Modules' TAB to help when temperature coefficiences are not in %/°C or %/°K but in mV/°C or mA/°C
1.7 | - Added new solar modules, voltage drop correction and an option to rise the cell temperature in the example list, when the solar modules do not see snow and therefor temperatures will not be so low.
1.6 | - Inserted 4 new regulators and 2 more custom module.
1.5 | - Inserted 4 languages @ updated not applicable (N.A.) voltages for 75/15, 75/50 & 100/15.
1.4 | - Changed texts and Module temperature window.
1.3 | - Power reduction comment set @ highest temperature.
1.2 | - Reduced output current to maximum output current at low & high temperatures. Now a system will show 'power loss' only wenn the output current exceeds the max. at low & high temperatures.
1.1 | - Inserted BlueSolar MPPT 100/15. Inserted custom module
1.0 | - First version
0.1 | - This Excel gives an indication how to calculate Victron Energy MPPT's

## Language (hidden)
V
Pos. | ENGLISH | DUTCH | ESPANGOL | DEUTSCH | FRANCAIS
1 | Module: | Paneel: | Módulo FV: | Modul: | Panneau:
2 | In series: | In serie: | Cuantos módulos? En Serie: | In Reihe: | En serie:
3 | Parallel: | Parallel: | En paralelo: | Parallel: | Parallèle:
4 | Total PV power @STC: | Totale PV vermogen @STC: | Potencia total FV @STC: | PV Leistung insgesamt @STC: | Puissance PV totale @STC:
5 | Wp | Wp | Wp | Wp | Wc
6 | Module temperature: | Paneel temperatuur: | Temp. módulo FV | Modul Temperatur: | Température Paneau:
7 | Min. | Min. | Min. | Min. | Min.
8 | Max. | Max. | Max. | Max. | Max.
9 | Controller: | Regelaar: | Reguladorr: | Regler: | Régulateur:
10 | System voltage: | Systeem spanning: | Voltaje del sistema: | System Spannung: | Tension du système:
11 | Max. input voltage | Max. ingangsspanning | Voltaje max. de entrada | Max. Eingangspannung: | Tension d'entrée max.:
12 | Max. PV voltage @ min. temperature | Max. PV spanning @ min. temp. | Voltaje max. FV @ Temperatura min. | Max. PV Spannung @ min. Temp. | PV tension max. @ temp. min.
13 | Min. input voltage @ MPP | Min. ingangsspanning @ MPP | Voltaje min. de entrada @ PMP | Min. Eingangspannung @ MPP | Tension d'entrée min. @ MPP
14 | Min. PV voltage @ max. temperature | Min. PV spanning @ max. Temp. | Voltaje min. FV @ Temperatura max. | Min. PV Spannung @ max. Temp. | PV tension min. @ temp. max.
15 | Max. output current | Max. uitgangsstroom | Corriente max. de salida | Max. Ausgangstrom | Courant de sortie max.
16 | Max. current @ MPP min. temp. | Max. stroom @ MPP min. temp. | Corriente max. @ PMP temp. min. | Max. Strom @ MPP min. Temp. | Courant max. @ MPP temp. min.
17 | Max. current @ MPP max. temp. | Max. stroom @ MPP max. temp. | Corriente max. @ PMP temp. max. | Max. Strom @ MPP max. Temp. | Courant max. @ MPP temp. max.
18 | Solar module configuration | Zonne-paneel configuratie | Configuración del módulo FV | Solar Modul Auslegung | Configuration du panneau
19 | Example locations with expected temperatures: | Voorbeeld lokaties en verwachte temperatuur: | Ejemplos de lugares con temperaturas previstas: | Beispiel Standort und erwartete Temperatur: | Exemple de localisation de site avec la température attendue:
20 | Flat on mobile home, all year (poor ventilation) | Vlak op camper, gehele jaar (slechte ventilatie) | Plano sobre una autocaravana, durante todo el año (mala ventilación) | Flach auf Wohnmobil, ganze Jahr (schlechte Hinterlüftung) | À plat sur toit de camping-car toute l'année (mauvaise ventilation)
21 | Flat on mobile home, only summer (poor ventilation) | Vlak op camper, alleen zomers (slechte ventilatie) | Plano sobre una autocaravana, sólo en verano (mala ventilación) | Flach auf Wohnmobil, nur Sommer (schlechte Hinterlüftung) | À plat sur camping-car , seulement l'été (mauvaise ventilation)
22 | Flat on boat (poor ventilation) | Vlak op boot (slechte ventilatie) | Plano sobre el techo de un barco (mala ventilación) | Flach auf Boot (schlechte Hinterlüftung) | À plat sur ​​le bateau (mauvaise ventilation)
23 | Pitched on boat (good ventilation) | Onder helling op boot (goede ventilatie) | Inclinado sobre el techo de un barco (buena ventilación) | Geneigt auf Boot (gute Hinterlüftung) | Inclinée sur bateau (bonne ventilation)
24 | Pitched roof in warm region (good ventilation) | Op schuin dak warme omgeving (goede ventilatie) | Techo inclinado en una región cálida (buena ventilación) | Schrägdach, warme Umgebung (gute Hinterlüftung) | Toit en pente, en région chaude (bonne ventilation)
25 | Pitched roof in average region (good ventilation) | Op schuin dak gemiddelde omgeving (goede ventilatie) | Techo inclinado en una región templada (buena ventilación) | Schrägdach, mittlere Regio (gute Hinterlüftung) | Toit en pente, région tempérée (bonne ventilation)
26 | Pitched roof on mountain (good ventilation) | Op schuin dak in de bergen (goede ventilatie) | Techo inclinado en las montañas (buena ventilación) | Schrägdach, in Bergen (gute Hinterlüftung) | Toit en pente, en montagne (bonne ventilation)
27 | * Power limiting @ low temp. | * Vermogens begrenzing @ lage temp. | * Reducción de potencia @ Temp. baja | * Leistung Begrenzung @ niedrige Temp. | * Limitation de puissance @ basse temp.
28 | ** Power limiting @ high temp. | ** Vermogens begrenzing @ hoge temp. | ** Reducción de potencia @ Temp. alta | ** Leistung Begrenzung @ hohe Temp. | ** Limitation de puissance @ haute temp.
29 | Input voltage window | Ingangspanning venster | Ventana de voltaje | Eingangspannungsfenster | Fourchette de tension
30 | Charge current window | Laadstroom venster | Ventana de corriente | Ladestromfenster | Fourchette de courant
31 | Cable length, Module to MPPT * | Kabel lengte, paneel tot MPPT * | Largo de cable entre modulo y MPPT * | Kabel Länge, Modul zum MPPT * | Longueur cable, Paneaux à MPPT *
32 | Cross-section: | Doorsnede: | Sección: | Querschnitt: | Section:
33 | * One way length | * Enkele afstand | * Longitud de un solo cable | * Einfache Distanz | * La distance simple
34 | Are the solar modules covered with snow many periods a year? | Zijn de panelen gedurende veel periodes bedekt met sneeuw? | ¿Los módulos están cubiertos con nieve durante muchos períodos del año? | Sind die Solar Module öfters im Jahr bedeckt mit Schnee? | Les panneaux PV sont-ils souvent couverts de neige ?
35 | Yes | Ja | Si | Ja | Oui
36 | No | Nee | No | Nein | Non
37 | Accepted | Toegestaan | Aceptado | Erlaubt | Accepté
38 | NOT accepted | NIET toegestaan | NO aceptado | NICHT erlaubt | PAS accepté
39 | Attention: More than 30% oversized PV generator | Attentie: Meer dan 30% overgedimensioneerde PV generator | Atención, se ha sobredimensionado el generador FV más del 30% | Achtung: Mehr als 30% überdimensionierte PV Generator | Attention, surdimensionnement PV supérieur à 30% ! Non recommandé financièrement !
40 | Coefficient support: | Koefficient berekening: | Calculación de coeficiente de temperatura | Koeffizientenberechnung: | Coefficients de température:
41 | If you have the voltage temperature coefficient in mV/°C, here is how to change it to %/°C | Hier kunt U de spanning koeffizient van mV/°C naar %/°C omrekenen | Si tiene el coeficiente de temperatura de voltaje en mV/°C, aquí es cómo cambiarlo a %/°C | Hier können Sie die Spannungskoeffizient von mV/°C in %/°C wandeln | Si vous avez le Coefficient de température à tension de circuit ouvert en mV/°C , voici comment changer ce coefficient en %/°C
42 | Write the Voc value in Volt: | Schrijf hier de Voc waarde in Volt: | Escribir el valor de Voc (voltage de circuito abierto) en voltios | Schreiben Sie den Voc Wert in Volt: | Ecrire la valeur de la VOC en Volt:
43 | Write the coefficient value in mV/°C: | Schrijf hier de koefficient waarde in mV/°C: | Escribir el valor de coeficiente en mV/°C: | Schreiben Sie den Koeffizient Wert in mV/°C: | Ecrire la valeur du coefficient en mV/°C:
44 | The coefficent value in %/°C is now: | De berekende koefficient in %/°C is nu: | El valor de coeficiente en %/°C es ahora: | Der errechneter Koeffizient in %/°C ist jetzt: | La valeur du coefficient en %/°C est de:
45 | If you have the current temperature coefficient in mA/°C, here is how to change it to %/°C | Hier kunt U de stroom koeffizient van mA/°C naar %/°C omrekenen | Si tiene el coeficiente de temperatura actual en mA/°C, aquí es cómo cambiarlo a %/°C | Hier können Sie die Stromkoeffizient von mA/°C in %/°C wandeln | Si vous avez le Coefficient de température à Courant de Court-Cicuit en mA/°C, voici comment changer ce coefficient en %/°C
46 | Write the Isc value in Ampere: | Schrijf hier de Isc waarde in Ampere: | Escribir el valor de Isc (corriente de cortocircuito) en amperios | Schreiben Sie den Isc Wert in Ampere: | Ecrire la valeur de Isc en Ampère:
47 | Write the coefficient value in mA/°C: | Schrijf hier de koefficient waarde in mA/°C: | Escribir el valor de coeficiente en mA/°C: | Schreiben Sie den Koeffizient Wert in mA/°C: | Ecrire la valeur du coefficient en mA/°C:
48 | The coefficent value in %/°C is now: | De berekende koefficient in %/°C is nu: | El valor de coeficiente en %/°C es ahora: | Der errechneter Koeffizient in %/°C ist jetzt: | La valeur du coefficient en %/°C est de :
49 | Warning: PV current is higher than MPPT max. input current | Waarschuwing: PV stroom is hoger dan max. ingangstroom MPPT | Atención: la corriente FV es superior a la máxima corriente de entrada MPPT | Warnung: PV Strom ist höher als max. erlaubter Eingangstrom MPPT | Attention! Le courant PV est supérieur au courant d’entrée maximum du MPPT